There is a new system that has been implemented into Panel Mate to control and monitor the dry nitrogen line going into our desiccators. The nitrogen line was redone as shown below to have a Panel Mate controlled flow as well as a manual line, hand controlled flow path. The controller has a default to open, so if it were to lose power or become disconnected it would continue to allow the nitrogen through the line. The new plumbing is located in the Gamma Lab at the end of the hall. When you walk in the door, it is in the top corner over your left-hand shoulder.

It is important to keep in mind that this line will control the nitrogen to all three labs in our hallway, not just the HiRA lab, i.e. if we close the valve, none of the labs in our wing will get dry nitrogen.

To access the Panel Mate controller for this line, you need to open the file “BuildingPLC.MT2”. The page of interest to us is Page 9 titled Dry N2 Humidity. We are interested in the two rightmost columns of information, those involving EV9019. The top circle tells you whether or not the Valve is open (open indicates that nitrogen is flowing to the desiccators). When this button is clicked more buttons will pop up on the right allowing you to close the valve if need be. The middle oval shows the % of humidity and the level of humidity that will trip the alarm. The bottom oval indicates the temperature in the desiccators. There is also a voice alarm so that if the alarm gets tripped the control room will notify the contacts for the group.